## Sheet1
Conductors in Raceway in Free Air | 3 - No. 2 copper concentric | 3 - No. 2 copper concentric | 3 - No. 3/0 THWN copper concentric | 3 - No. 3/0 THWN copper concentric | 3 - 500 kcmil XHHW copper concentric | 3 - 500 kcmil XHHW copper concentric | 3 - No. 2 copper concentric | Conductors in Raceway in Free Air
Locked cells are in color | stranded in 1 inch EMT | stranded in 1 inch schedule 80 | stranded in 11/2 inch EMT | stranded in 11/2 inch SCH 80 PVC | stranded in 3 inch EMT | stranded in 3 inch SCH 80 PVC | stranded in 1 inch EMT | Locked cells are in color
Variable cells are white | 30 degree ambient ref. | 30 degree ambient ref. | 30 degree ambient ref. | 30 degree ambient ref. | 30 degree ambient ref. | 30 degree ambient ref. | 30 degree ambient ref. | Variable cells are white
Insulation Thickness from NEC Table 310-13 | 0.045 | 0.045 | 0.05 | 0.05 | 0.065 | 0.065 | 0.045 | Insulation Thickness from NEC Table 310-13
Conductor Diameter from NEC Table 8 Chapt 9 | 0.292 | 0.292 | 0.47 | 0.47 | 0.813 | 0.813 | 0.292 | Conductor Diameter from NEC Table 8 Chapt 9
DI outside conductor Diameter | 0.382 | 0.382 | 0.57 | 0.57 | 0.943 | 0.943 | 0.382 | DI outside conductor Diameter
Insulation Degrees C - cm / Watt | 400 | 400 | 500 | 500 | 500 | 500 | 400 | Insulation Degrees C - cm / Watt
RI Conductor Insulation Thermal Ohm Feet | 0.56007 | 0.56007 | 0.50266 | 0.50266 | 0.38653 | 0.38653 | 0.56007 | RI Conductor Insulation Thermal Ohm Feet
Number of Conductors | 3 | 3 | 3 | 3 | 3 | 3 | 3 | Number of Conductors
Factor A' from Table VII N-M | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | Factor A' from Table VII N-M
Factor B' from Table VII N-M | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | 0.19 | Factor B' from Table VII N-M
Multiplier for Ds from Table VII Notes | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | 2.15 | Multiplier for Ds from Table VII Notes
DI (conductor diameter from above) | 0.382 | 0.382 | 0.57 | 0.57 | 0.943 | 0.943 | 0.382 | DI (conductor diameter from above)
Ds (multiplier x DI)) | 0.8213 | 0.8213 | 1.2255 | 1.2255 | 2.0274 | 2.0274 | 0.8213 | Ds (multiplier x DI))
Rsd | 9.4927 | 9.4927 | 6.7821 | 6.7821 | 4.3293 | 4.3293 | 9.4927 | Rsd
Calculation of Rd for duct wall | [7 empty] | Calculation of Rd for duct wall
Thermal Conductivity in W / m-C (71 for iron, 130 for Al, and 0.16 for PVC) | 71 | 0.16 | 71 | 0.16 | 71 | 0.16 | 71 | Thermal Conductivity in W / m-C (71 for iron, 130 for Al, and 0.16 for PVC)
t thickness of duct wall | 0.057 | 0.179 | 0.065 | 0.2 | 0.072 | 0.3 | 0.057 | t thickness of duct wall
Duct wall thermal resistance in C -cm / Watt | 1.4085 | 625 | 1.4085 | 625 | 1.4085 | 625 | 1.4085 | Duct wall thermal resistance in C -cm / Watt
Outside Diameter of Duct or raceway | 1.163 | 1.315 | 1.74 | 1.9 | 3.5 | 3.5 | 1.163 | Outside Diameter of Duct or raceway
Rd thermal ohm feet calculation | 0.0022647 | 3.0726 | 0.0017053 | 2.2941 | 0.00092297 | 1.8281 | 0.0022647 | Rd thermal ohm feet calculation
Ds' (conduit O.D.) from manufacture | 1.163 | 1.315 | 1.74 | 1.9 | 3.5 | 3.5 | 1.163 | Ds' (conduit O.D.) from manufacture
e (emissivity) | 0.95 | 0.95 | 0.95 | 0.3 | 0.95 | 0.3 | 0.95 | e (emissivity)
N (number of conductors) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | N (number of conductors)
Re | 7.726 | 7.054 | 5.674 | 8.6539 | 3.1346 | 5.4551 | 7.726 | Re
RCA (Sum of Ri + Rsd +Rd+ Re) | 17.781 | 20.1794 | 12.9605 | 18.2328 | 7.8514 | 11.999 | 17.781 | RCA (Sum of Ri + Rsd +Rd+ Re)
Circular mil area for calculating resistance using NM | 66360 | 66360 | 167800 | 167800 | 500000 | 500000 | 66360 | Circular mil area for calculating resistance using NM
Circular mil ohms per foot at 75 degrees C. (enter 12.9 for copper and 21.2 for aluminum) | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | Circular mil ohms per foot at 75 degrees C. (enter 12.9 for copper and 21.2 for aluminum)
RDC Calculated using NM for Temperature TC | 203.8156 | 203.8156 | 76.8772 | 76.8772 | 27.0504 | 27.0504 | 203.8156 | RDC Calculated using NM for Temperature TC
75 degree C. AC Resistance from NEC Chapter 9 Table 9 Cols 4-6 Reference | 0.2 | 0.19 | 0.079 | 0.077 | 0.029 | 0.027 | 0.2 | 75 degree C. AC Resistance from NEC Chapter 9 Table 9 Cols 4-6 for Reference
75 degree C. DC Resistance from Chapter 9 Table 8 Reference | 0.194 | 0.194 | 0.076 | 0.076 | 0.0258 | 0.0258 | 0.194 | 75 degree C. DC Resistance from Chapter 9 Table 8 for Reference
AC/DC Ratio from Standard Handbook for Electrical Engineers | 1 | 1 | 1.04 | 1.002 | 1.13 | 1.018 | 1 | AC/DC Ratio from Standard Handbook for Electrical Engineers
AC Resistance corrected for temperature | 203.8156 | 203.8156 | 79.9523 | 77.031 | 30.567 | 27.5373 | 203.8156 | AC Resistance corrected for temperature
TC (maximum insulation temperature degrees C) | 90 | 90 | 75 | 75 | 90 | 90 | 90 | TC (maximum insulation temperature degrees C)
TA (ambient temperature) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | TA (ambient temperature)
Ambient derating factor to compare to Table 310-16 - use upper limit | 100% | 100% | 100% | 100% | 100% | 100% | 100% | Ambient derating factor to compare to Table 310-16 - use upper limit
Amperes from N-M Calculation | 128.6703 | 120.7822 | 208.3918 | 178.9976 | 500.0078 | 426.1299 | 128.6703 | Amperes from N-M Calculation
Thermal Derating Factor using N-M Equation brought up from below | 80.93% | 83.21% | 66.12% | 78.13% | 76.11% | 88.32% | 80.93% | Thermal Derating Factor using N-M Equation brought up from below
Thermal Derating Factor using R-Value for same insulation | 80.74% | 83.03% | 67.16% | 78.13% | 76.11% | 88.32% | 80.74% | Thermal Derating Factor using R-Value for same insulation
Recalculation with outside thermal insulation using N-M equations | [7 empty] | Recalculation with outside thermal insulation using N-M equations
RCA minus Re from above | 10.0551 | 13.1254 | 7.2864 | 9.5788 | 4.7167 | 6.5439 | 10.0551 | RCA minus Re from above
Thermal thickness in inches (variable) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Thermal thickness in inches (variable)
Total insulation addon to outside diameter (2 x thickness) DI'' | 2 | 2 | 2 | 2 | 2 | 2 | 2 | Total insulation addon to outside diameter (2 x thickness) DI''
Raceway O.D. from above DC'' | 1.163 | 1.315 | 1.74 | 1.9 | 3.5 | 3.5 | 1.163 | Raceway O.D. from above DC''
Thermal insulation thermal conductivity BTU - in / hr - ftsqd-degrees F | 0.32 | 0.32 | 0.17 | 0.17 | 0.32 | 0.32 | 0.32 | Thermal insulation thermal conductivity BTU - in / hr - ftsqd-degrees F 0.32 for fiberglass, .17 for polyurethane
Thermal conductivity in Watts/cm-degrees (above x .00144131) | 0.00046122 | 0.00046122 | 0.00024502 | 0.00024502 | 0.00046122 | 0.00046122 | 0.00046122 | Thermal conductivity in Watts/cm-degrees (above x .00144131)
Thermal Resistance (1/conductivity) in degrees-cm/Watt | 2168.1665 | 2168.1665 | 4081.2545 | 4081.2545 | 2168.1665 | 2168.1665 | 2168.1665 | Thermal Resistance (1/conductivity) in degrees-cm/Watt
RI'' thermal ohm feet for insulation | 11.3053 | 10.4477 | 16.2755 | 15.2954 | 5.1072 | 5.1072 | 11.3053 | RI'' thermal ohm feet for insulation
Calculation of Re''' for outside thermal insulation | [7 empty] | Calculation of Re''' for outside thermal insulation
Ds''' outside diameter of thermal barrier | 3.163 | 3.315 | 3.74 | 3.9 | 5.5 | 5.5 | 3.163 | Ds''' outside diameter of thermal barrier
e''' emissivity .3 for dull, .95 for foil covered) | 0.32 | 0.32 | 0.17 | 0.3 | 0.3 | 0.3 | 0.32 | e''' emissivity .3 for dull, .95 for foil covered)
Re''' | 5.7865 | 5.573 | 6.0798 | 4.9936 | 3.7311 | 3.7311 | 5.7865 | Re'''
RCA''' (RCA-Re+RI'''+Re''') | 27.1469 | 29.1462 | 29.6417 | 29.8679 | 13.555 | 15.3822 | 27.1469 | RCA''' (RCA-Re+RI'''+Re''')
New ampacity with thermal insulation | 104.1351 | 100.5 | 137.7967 | 139.8528 | 380.539 | 376.3614 | 104.1351 | New ampacity with thermal insulation
Degrees F | 212 | 212 | 160 | 160 | 160 | 160 | 212 | Degrees F
Conversion from Degrees F to Degrees C | 100 | 100 | 71.1111 | 71.1111 | 71.1111 | 71.1111 | 100 | Conversion from Degrees F to Degrees C
Degrees C | 90 | 90 | 32 | 75 | 90 | 90 | 90 | Degrees C
Conversion of degrees C. to degrees F | 194 | 194 | 89.6 | 167 | 194 | 194 | 194 | Conversion of degrees C. to degrees F
Thermal Derating Factor using N-M equations | 80.93% | 83.21% | 66.12% | 78.13% | 76.11% | 88.32% | 80.93% | Thermal Derating Factor using N-M equations
Calculation Below Using R-Value for one inch of insulation | [7 empty] | Calculation Below Using R-Value for one inch of insulation
RCA minus Re from above | 10.0551 | 13.1254 | 7.2864 | 9.5788 | 4.7167 | 6.5439 | 10.0551 | RCA minus Re from above
Thermal thickness in inches (variable) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Thermal thickness in inches (variable)
Total insulation addon to outside diameter (2 x thickness) DI'' | 2 | 2 | 2 | 2 | 2 | 2 | 2 | Total insulation addon to outside diameter (2 x thickness) DI''
Raceway O.D. from above DC'' | 1.163 | 1.315 | 1.74 | 1.9 | 3.5 | 3.5 | 1.163 | Raceway O.D. from above DC''
R value for one inch of insulation in BTUth-in / hr-ft*ft-F | 3.125 | 3.125 | 5.883 | 5.883 | 3.125 | 3.125 | 3.125 | R value for one inch of insulation in BTUth-in / hr-ft*ft-F
693.81 times R-Value to convert to degrees-cm/Watt) | 2168.1562 | 2168.1562 | 4081.6842 | 4081.6842 | 2168.1562 | 2168.1562 | 2168.1562 | 693.81 times R-Value to convert to degrees-cm/Watt)
RI'' thermal ohm feet for insulation | 11.3053 | 10.4477 | 16.2772 | 15.2971 | 5.1072 | 5.1072 | 11.3053 | RI'' thermal ohm feet for insulation
Calculation of Re''' for outside thermal insulation | [7 empty] | Calculation of Re''' for outside thermal insulation
Ds''' outside diameter of thermal barrier | 3.163 | 3.315 | 3.74 | 3.9 | 5.5 | 5.5 | 3.163 | Ds''' outside diameter of thermal barrier
e''' emissivity .3 for dull, .95 for foil covered) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | e''' emissivity .3 for dull, .95 for foil covered)
Re''' | 5.9156 | 5.6986 | 5.1685 | 4.9936 | 3.7311 | 3.7311 | 5.9156 | Re'''
RCA''' (RCA-Re+RI'''+Re''') | 27.276 | 29.2717 | 28.7321 | 29.8695 | 13.555 | 15.3822 | 27.276 | RCA''' (RCA-Re+RI'''+Re''')
New ampacity with thermal insulation using R-Value | 103.8883 | 100.2843 | 139.9609 | 139.8491 | 380.5393 | 376.3617 | 103.8883 | New ampacity with thermal insulation using R-Value
Thermal Derating Factor with R-Value | 80.74% | 83.03% | 67.16% | 78.13% | 76.11% | 88.32% | 80.74% | Thermal Derating Factor with R-Value